## Quick Pick
see tab LED Em for Surelites
Assurance to Bodine cross reference
| Assurance Model | Hubbell Dual-Lite | ISO-Lite | Bodine Model | Iota | Notes
LED Emergency Driver | Constant Power | Limited portfolio | Limited Portfolio
| L4-A ( 4W, small) |  |  | BSL4L (4W)
| L5-CEC (5W) |  |  | BSL4L (4W) | ILB-CP05 | no conduit
| L10-DC-CEC | PLD7 / PLD7M(2) | EMP7-TS-F2 | BSL17C-C2 | ILB-CP07 (7W) -A | Assurance L10-CEC & L10-DC-CEC constant power (10W) output for 90 minutes. Price advantage compared to Bodine
Bodine B17C-C2 regulated power output: 7W initial, 4.5 W at 90 minutes
| L10-CEC (10W) | PLD10 |  | BSL310 | ILB-CP10 | Assurance L10-CEC 10W constant power output for 90 minutes. Price advantage compared to Bodine
Can have -SC opt | L10-DC-CEC (dual Conduit) | PLD10M (single Conduit) |  | BSL310-CDF | ILB-CP10-A | Bodine BSL310 regulated power output: 10W initial, 6 W at 90 minutes.
Com | L10-DC-CEC-SD & L10-CEC-SD |  |  | BSL10LST (310LP) |  | Self-diagnostic-Self Test 10 W
| L10-NP-CEC (10W) |  |  | BSL310LP | ILB-SL CP10 HE | Bodine not constant power
L9-ET-C-IP66
| L10-DC-2H (10W 2 hour) | PLD9M (9W) |  |  | ILB-CP07 2H (7W) | Iota only 7W not 10…
| L14-DC-CEC (14W) |  | EMP12-TS-F2 |  | ILB-CP-12(12W)
| L14-DC-CEC (14W) |  |  | BSL10M / BSL10C |  | Assurance 14W constant power output for 90 minutes. ILB is Constant Power
L14-CEC ( no conduit)
| L10-CEC-SBN ( separate Battery) |  |  | BSL310SB |  | Separate battery unit
Can have -SC opt | L20-DC-CEC (20W) |  |  | BSL20-LV | ILB-CP20 | Assurance L20--DC-CEC. Constant Power, Price and size advantage compared to Bodine.
| L30-DC-CEC |  | EMP25-TS-F2 | BSL20LV |  | Assurance L25-DC-CEC (25W),compact size - 1/2 size and weight compared to Bodine BSL20LV (20W). Price advantage compared to Bodine.
L30-C-480
| L10-ET-CEC (10W Cold temp) |  |  | BSL10Cold |  | Bodine much larger than Assurance EM.
| L30-C-HVO ( Class 1 out 55-255 Vdc) |  |  | BSL20MV or BSL20HV | ILBLPCP30HESDHV | Class 2
| L30-C-HVO-480 ( 480 V input/ Class 1 output 50-255 Vdc) |  |  |  | ILBHICP30HESDHV | Class 1 out - 480 V input Available - 8/23
No equal | L20-CB48 |  |  |  |  | Central Battery System EM Driver (48Vdc)
|  | Limited portfolio | Limited Portfolio
UL924 | ALCR-D5 ( alternate ALCR-D10L) | ATSD (not dim compatible) |  | GTD | ETS-DR | Assurance ALCR-D10L is 0-10VDC compatible - need 2 GTD for 0-10 dimming
Load | ALCR-D10-L (-PW with PLENUM TEST SWITCH HARNESS) |  |  | none | ETS-DR-A | Bodine: For 0-10VDC dimming, two GTD’s are required & do not have a Conduit Model
Control | ALCR-D10L (-PW with PLENUM TEST SWITCH HARNESS) | ELCR (5A only) |  | GTD10DIM |  | ALCR-D10 direct cross to Bodine GTD10DIM, alternate ALCR-D10L
Relays | ALCR-D20 |  | ELCD-924 (LVS) | GTD16DIM |  | ALCR-D20 direct cross to Bodine GTD16DIM, Alternate ALCR-D20L-C
| ALCR-D20L (-PW with PLENUM TEST SWITCH HARNESS) | ALCR1277
| ALCR-D10L(-PW with PLENUM TEST SWITCH HARNESS) |  |  | GTD | iis-35-I (no Pshare)
| ALCR-D5L-C-PST |  |  |  |  | No Bodine offering
ELCD-FD
UL1008 | BECELTS20 | ASTD20 | ELCD-1008 (ETC) | GTD20A |  | UL 1008 Transfer Device ( 20A)
| Si-10-PST ( w Power Share- max. connected load 50W) |  |  | Eli-S-10C |  | Si-10-PST: auto adjust to 10 W - Power Share with 0-10V dimming, mutiple fixtures(max 50W connected load)
| Si-35-PST ( w Power Share- max connected load 175W) | UFO-LED25 (no PShare) |  | ELI-S-20 (no Pshare) | iis-35 ( no Power S) | Si-35-PST: auto adjust to 35 W - Power Share with 0-10V dimming, mutiple fixtures(max 175W connected load)
| Si-23-PST ( w Power Share- max. connected load 115W) | LPS32 |  |  |  | Si-23-PST: auto adjust to 23 W - Power Share with 0-10V dimming, mutiple fixtures(max 115W connected load)
| S-50-PST ( w Power Share- max. connected load 150W) |  |  |  |  | SI-50-PST 50W inverter with Power Share ( auto Adjust , max. connected 0-10 vdc driver load- 150W) UPGRADE in 2026 wo t0 250W Max.
| Si-100-PST ( w PST, max. connected load 300W) |  |  |  |  | SI-100-PST 100W inverter with Power Share ( auto Adjust , max. connected 0-10 vdc driver load- 500W)
| Si-200-PST ( w Power Share- max. connected load 900W) |  |  |  | iis-50 ( no PST feature) | SI-200-PST 200W inverter with Power Share ( auto Adjust , max. connected 0-10 vdc driver load- 9000W)
| Si-125 (-PST Optional - 3 zones max. 375W) | LG125 | E3mini-125 | ELI-S-100 | iis-125-sm | ELI-S-100 auto dimming output, Assurance Si 125-PST Optional. Si-125 features self testing/diagnostics, ELI-S-100 does not.
Inverters | Si-250 (-PST Optional - 3 zones max. 375W) | LG250 | E3mini-250 | ELI-S-250 |  | ELI-S-250 - auto dimming output, Assurance Si 250-PST optional. Si-250 features self testing/diagnostics, ELI-S-250 does not.
| Si-375 (-PST Optional - 3 zones max. 1125W) | LG375 | E3-300 | ELI-S-400 | iis-375-LED | Assurance Si-400 direct cross to Bodine ELI-S-400
| Si-550 (-PST Optional - 3 zones max. 1125W) | LG600 | E3-500 | No equal | iis-550-I | No Bodine offering
| Si-750 (-PST Optional - 4 zones max. 2400W) | LG750 |  |  | iis-750
| Si-950 (-PST Optional - 4 zones max. 3120W) | LG950 | EX3-750 |  | iis - 1000
| Si-1150 (-PST Optional - 4 zones max. 4140W) | LG1150 | E3MAC-100
| BAL1400ACTD |  |  | B50 | I-320
| BAL1400ACTD | UFO-6W |  | B50 | I-232 | Assurance models operate 2 lamps in emergency
Fluorescent | [5 empty] | Bodine B50 output is series, so both lamps must be operating.
Emergency |  | UFO-5AW |  | B60 | I-48 | Direct cross to Bodine
Ballasts | BAL700TD | UFO-5W |  | B90 | I-40 | Direct cross to Bodine
| BAL500TD | UFO-3AW |  | B100 | I-32 | Direct cross to Bodine
| BALT51300ACTD | UFO-LP2 |  | LP600 | ISL-540 | Direct cross to Bodine
| BALT5-800TD | UFO-LP1 |  | LP550 | ISL-54 | Direct cross to Bodine
| BAL650C-4ACTD | UFO-CF1 |  | B94CGU | I-42-EM-A | Direct cross to Bodine
BALT5-500TD
NOTE: REM- DEM- HPEM type products are not listed on this reference
2025-10-01

## LED EM Drivers
All are Constant Power | AEL (Wattage) | Most all are regulated power |  | - HE option is for Title 20 California
Assurance LED EM Drivers |  | Bodine | Dual-Lite | Iota | Cooper- Sure-Lites | Feature
L4-A (no conduit- small) | 4 | BSL4L ( 4W)
L5-CEC (No conduit) | 5 | BSL4L ( 4W) |  | ILB-CP05
L9-C-ET-IP66 ,COLD -40C, IP66 w conduit | 9 |  |  | ILBDW10
L10-DC-CEC with dual conduit | 10 | BSL6LST Self-test |  | ILB-CP07 (7W) -A | EBPLED7 | Low/Narrow Profile
L10-DC-CEC-SD with dual conduit SD | 10 | BSL10LST Self-test & BSL310LPST |  |  | EBPLEDLP-10WSD/EBPLEDLP-7.5WSD | Low/Narrow Profile
L10-DC-CEC with dual conduit | 10 | BSL17C-C2 | PLD10M/PLD7M ( single Conduit) | ILB-CP10-A (can be -HE, dual conduit) |  |  | PLD7 / PLD7M(2)
L10-DC-CEC-SD with dual conduit -SD | 10 | BSL17C-C2ST Self Test |  |  | EBPLEDLP-7.5WSD
L10-CEC (no conduit) | 10 | BSL310 (poly case) | PLD10 |  |  |  | PLD10
L10-DC-CEC ( dual conduit) | 10 | BSL310M (Metal Case) | PLD10 | ILB-CP10 ( can be -HE) |  |  | PLD10M (single Conduit)
L10-NP-CEC ( narrow/low profile) | 10 | BSL310LP |  | ILB-SL CP10 HE |  | Low Profile
L10-CEC-SBN ( Separate Battery) | 10 | BSL310SB |  | ILBCP10LC ( DISCON)
L10-DC-2H (has dual Conduit) | 10 |  | PLD9M ( 9 W, 2hour) | ILB-CP07 2H -A(7W)
L14-CEC ( no conduit) | 14
L14-DC-CEC ( has dual Conduit) | 14 | BSL14B2UAK55DF |  | ILB-CP-12-A ( -HE-A , 12W)(15W also) | EBPLED14 ( has single conduit)
L20-DC-CEC ( dual conduit) | 20 | BSL20LV |  | ILBCP20HE | EBPLEDC1LV ( has single conduit |  | PLD9M (9W)
L10-ET-CEC (10 W Cold) | 10 | BSL36 Cold-Pak ( 6W only) |  |  |  | 0-55C
L10-ET-CEC (10 W Cold) | 10 | BSL10 Cold-Pak |  |  |  | 0-55C, much smaller
L30-DC-CEC remote dual conduit | 30 | BSL722 ( internal mounting)
L30-DC-CEC remote dual conduit | 30 | BSL722 Cold Pak ( internal mounting)
L30-DC-CEC remote dual conduit | 30 | BSL718 |  | ILB-CP20-A
BSL8SB
BSL310HAZ
BSL310HAZSB
L9-C-ET-IP66 Q3-2024, -40C, IP66 w conduit | 9
BSL17 & BSL17C
L30-C-HVO (30W) | 30 | BSL20MV |  | ILBLPCP30HESDHV
L30-C-HVO (30W) | 30 | BSL20HV |  |  | EBPLEDc1-HV
L30-C-HVO-480 | 30 |  |  | ILBHICP30SDHV (SD)
no equal by others
L20-CB48 48 Vdc systems | up to 20W |  |  |  |  | Telephone Call center (-48 VDC)
L10-DC-CEC-SC (Special lead length for CBT- flat panel) | 10 |  |  |  |  | CBT Luminaires
L14-DC-CEC-SC (Special lead length for CBT- flat panel) | 14 |  |  |  |  | CBT Luminaires
L20-DC-CEC-SC (Special lead length for CBT flat panel | 20 |  |  |  |  | CBT Luminaires
DC= Dual Conduit |  |  |  | -A for Iota is dual conduit
NP= Narrow /Low Profile
ET= Cold Temp
Note on F7: 10W is LP and no conduit 7.5 is not LP but has dual conduit - both Self-Diagnostic

## INVERTERS
Inverters
| Assurance | AEL Max Connected Load | Bodine | Bodine Max. Connected Load | Dual-Lite | Isolite | Iota | Myers | Emergi-Lite | Lightalarms | Evenlite | Sure Lites | Online Power | Perfect Power
| Si-10-PST | 50W | ELI-S-10 | 50W
| Si-23-PST | 115W | ELI-S-20/25 | 25W/? | LPS20 | MPS20 | IIS-25 | LVU-25 |  |  |  | INV-20 | 27REI
| Si-35-PST | 175W | NA |  | LPS32, LPS35 | MPS32, MPS35 | IIS-35 |  | EMILC-32 | LMILC-32 | MIP-36 | INV-35 | 36REI
| Si-50-PST | 150W | Eli-50 |  | LPS55 | MPS55 | IIS-50 | LVU-50 | EMLIC-55 | LMLIC-55 |  | INV-55
target Q2 2025 | Si-100-PST | 500W | Eli-S-100 | 400W | LG125S (110W) | E3MINI-125 | IIS-125 | LVM-125 | EMIU-125 | LMIU-125 | PWII-12/MIP100 | INV-110
| Si-200-PST | 900W | NA |  | LG250S (220W) | E3MINI-250 | IIS-250 | LVM-250, IE-1.5, LV-1 | EMIU-250 | LMIU-250 | PWII-25 | INV-220 | 200REI, WM.2A/R | WM.2A/R
| Si-125** | 375 W-PST Option | Eli-S-100 | 400W | LG-125S (110W) | E3MINI-125 | IIS-125 | IE-1.5, LVM-125 | EMIU-125 | LMIU-125 | PWII-12 | INV-110
| Si-250** | 375 W-PST Option | Eli-S-250 | 800W | LG250S (220W) | E3MINI-250 | IIS-250 | IE-2, LVM-250 | EMIU-250 | LMIU-250 | PWII-25 | INV-220
| Si-400, Si-375 | Si-375-PST: 1125W | Eli-S-400 |  | LG375 | ESMINI-375 | IIS-375 | LV-2 | EMIU-400 | LMIU-400 | PWII-37 | INV-375 | WM.3A/R | WM.3A/R
| Si-600, Si-550 | Si-550-PST: 1125W | NA |  | LG600 | E3MINI-550 | IIS-550 | LV-3 |  |  | PWII-55 | INV-600 | WM.5A/R | WM.5A/R
| Si-750 | Si-750-PST: 2400W | NA |  | LG750 | EX3-750 | IIS-750 | LV-4 | EMIU-720 | LMIU-720 |  |  | WM.7A/R | WM.7A/R
| Si-950 | Si-950-PST: 3120W | NA |  | LG950 | E3MAC-100 | IISC-1000 | IE-7
| Si-1150 | Si-1150-PST: 4140W | NA |  | LG1150 |  |  | IE-8, LV-5, EM-1 | EMIU-1000 | LMIU-1000 |  |  | WM1.0A/R | WM1.0A/R
| 750/950 and 1150 will need to wire multiple zones for max. load | [6 empty] | LV1=175W
**Self- Test Standard
PST: Power Share w 0-10 Vdc
**Self- Test Standard
Micro Inverters have auto adjust PST tomax. EM power when 0-10 Vdc Em dimming
PST is Optional on the Si-125 and Si-250 ( 3 circuits & 20/40/60/80/100% settable)
PST is standard on Si-200-PST Auto Adjust to 200W with 0-10 vdc driver loads ( 900W Max normal Power)
PST is standard on Si-10-PST Auto Adjust to 10W with 0-10 vdc driver loads ( 50W max normal load)
PST is standard on Si-23-PST Auto Adjust to 23W with 0-10 vdc driver loads ( 115W max normal load)
PST is standard on Si-50-PST Auto Adjustt to 50W with 0-10 vdc driver loads (150W max normal load) ( upgrade soon to 250W)
PST is standard on Si-100-PST Auto Adjust to 100W with 0-10 vdc driver loads ( 500W max normal load)
PST is standard on Si-35-PST Auto Adjust to 35W with 0-10 vdc driver loads ( 175W max normal load)

## Fluorescent EM
Fluorescent EMB
https://assurancelighting.com/products/fluorescent-ballasts.htm
NOTE_- CEC models are different - see website..
#VALUE!
Note: We have additional emegency ballast- Contact the factory for competitve choices.
BAL500TD
Contact AEL for Cross/replacement

## Emergency Relay Cross
Assurance Emergency Lighting | LUTRON LUT Series | LVS - EPC Series | HUB Controls | Bodine | Dual-Lite/Hubbell Controls | Iota | Wattstopper | EVENlite | ISOlite
ALCR-D20L (-PW), ALCR-D20 For JBOX ELCD-FD | LUT-ALCR | EPC-2A | ALCR-1277 | BLCD16DIM, BLCD-20B (non dimming) |  | ETS-20 (8A only) | ELCU-200
ALCR-D10L, ALCR-D5, | LUT-ALCR-FM | EPC-2-FM | ALCR-1277 | GTD (3 AMPS,non dimming) | ATSD (3 AMPS, non-dimming), | ETS-DR (3A)
ALCR-D20L (-PW), ALCR-D20 | LUT-ALCR-D |  | UL924EPC1D-UNV** Flush mount in jbox
ALCR-D10L, ALCR-D5 | LUT-ALCR-D-FM |  | ALCR-1277 | GTD10DIM | UL924EPC1D-UNV, UL924BR-UNV ( non-dimming)
| LUT-ALCR-DMX | EPC-DMX
ASR120/ASR277/ALCR-D20L (-PW) | LUT-Shunt | RRUSR1/RRUSR2 | UL924SR1 (120v)/SR2 (277v) |  | UL924SR1
ASR120/ASR277/ALCR-D10L | LUT-Shunt-FM |  |  |  | UL924SR2
ALCR-D20L (-PW), ALCR-D20 | LUT-Shunt-D
ALCR-D10L, ALCR-D5 | LUT-Shunt-FM
GTDU (2A, UL1008)
| LUT-ALCR-D-HV-347V | EPC-1-D-HV
BECLTS20 (ETL-UL1008) | LUT-Shunt-A-TD | EPC-D-F-ATS |  | GTD20A (20A, UL1008) | BCCR20 or UL1008BCELTS1277
ALCR-D5L-C-PST | NO CROSS | No Cross
ELCD-FD |  |  | EPC-2D
ELCD-FD |  |  | EPC-2 ( no dim)
ALCR-D20L-PW |  |  | EPC-A-2-D
-C models have remote test switch included.
Note- Assurance Em devices do look different and features that are different than other mfgs. Please review spec sheets.
ALCR-D5 and ALCR-D20 (only) are Made In USA.
ALCR-D10L, ALCR-10L-PW, AlCR-20L, and ALCR-D20L-PW are NOT made in the USA but are TAA
GTDU- no cross

## more EM RELAYS
EM Relays
Assurance EM | Feature | Bodine | Dual-Lite/Hubbell Controls | Lutron/LVS | LVS
ALCR-D5, ALCR-D10L | 5A, 10A UL924 ALCR | GTD (3 AMPS,non dimming) | ATSD (3 AMPS, non-dimming), | LUT-ALCR , LUT-ALCR-D
ALCR-D10L | 10A, UL924 ALCR | GTD10DIM
ALCR-D20, ALCR-D20L (-PW) | 20A, UL924 ALCR | BLCD16DIM, BLCD-20B (non dimming) | UL924EPC1D-UNV, UL924BR-UNV ( non-dimming)
ASR120 ( can USE ALCR-D10L/20L -PW) | 10A, Shunt Bypass |  | UL924SR1
ASR277 (can use ALCR-D10L / D20L (-PW)) | 10A, Shunt Bypass |  | UL924SR2
BCELTS20 | 16A UL1008 | GTD20A (20A, UL1008) | BCCR20 or UL1008BCELTS1277
GTDU (2A, UL1008)
ALCR-D20L-PW | 20A, stud mount
ALCR-D10L-PW | 10A, stud mount
ALCR-D20L | 20A, Channel mounting
ALCR-D10L | 10A, Channel mounting -
ADDITIONAL MFG
ALCR-D5 replaces ALCR-D3
ALCR-D5 or ALCR-D10L replaces ALCR-d3